## Instructions
| PROJECT: | xxx | PROJECT NO.: | xxx
| CREATED BY: | xxx | CREATED DATE: | xxx
| CHECKED BY: | xxx | REVISED DATE: | xxx
Point-To-Point Fault Current Calculation
Description: |  | This spreadsheet calculates SCCR (Short Circuit Current Rating) or the available fault current at the switchboard, panelboard, or equipment. This calculation is typically intended for generating preliminary approximate values, for calculating panel AIC ratings during early project phases. This calculation is not for final equipment specification purposes. EasyPower should be utilized for final full-project calculations. If required by the project specifications, the Electrical Contractor is also to provide short circuit calculations during CA.
Instructions: |  | 1. Enter the project info at the top of this Instructions tab, and the Fault Current Calc tab.
2. Input the available fault current. This may be via your own calculations, or an available fault current
that is already known or confirmed by the utility.
3. Replace the content that is in orange text.
4. Make sure that the "I(sc)" cells are linked correctly to the available fault current or to the
"I(sc-sym rms)" column that panel or equipment is fed from.
5. To add more rows, copy & paste existing row information. DO NOT CREATE A NEW ROW;
formulas will not be copied over.
6. Double check that the referenced cells are linking/referencing correctly.
7. The calculation tab allows (1) voltage only. If (2) voltages are needed (for example, for the primary
and secondary sides of a transformer), make a copy of the "Fault Current Calc" tab, and select the 2nd
voltage in this new tab.
8. The available short circuit current at the secondary side of transformers can be conservatively
estimated using the infinite bus calculation:
Available short circuit current at transformer secondary = (Transformer FLA at
secondary) / (Transformer impedance)
Notes / Assumptions:
1. | User input cells (color 8)
2. | Default design criteria (color 5)
3. | Referenced values (color 6)
4. | Calculated values (black)
1.
2.
3.
4.
5.
6.

## Fault Current Calc
PROJECT: | xxx |  | PROJECT NO.: | xxx
CREATED BY: | xxx |  | CREATED DATE: | xxx
CHECKED BY: | xxx |  | REVISED DATE: | xxx
Point to Point 3-Phase Bolted Fault Current Calculation
Panel & Equipment Calculation Area
Available Fault Current: | 101000
Voltage: | 480
Safety Factor - 95%
From | To | Length (ft) | I(sc) (FROM) | C value (total) | C value PER FEEDER | f (calc) | M (calc) | I(sc-sym rms) (TO) | Per Phase (# Conductors) | Conduit | Type (CU/AL) | Cable (Single/3C) | Wire Size (kcmil/AWG) | Busway Type | Busway Size | Notes | AIC Rating
"PANEL A (replace)" | "PANEL B (replace)" | 20 | 101000 | 296780 | 26980 | 0.02456 | 0.97603 | 98578.9292 | 11 | Steel | CU | 3C | 500 |  |  |  | 150000
"PANEL B (replace)" | "PANEL C (replace)" | 30 | 98578.9292 | 52864 | 26432 | 0.20186 | 0.83204 | 82021.9193 | 2 | Steel | AL | 3C | 750 |  |  |  | 100000
"PANEL C (replace)" | "AHU-1 (replace)" | 30 | 82021.9193 | 52864 | 26432 | 0.16796 | 0.8562 | 70226.8383 | 2 | Steel | AL | 3C | 750 |  |  |  | 100000
Note:
1. Minimum cable length required to stay with 10000AIC panel rating.

## "C" Conductors Values
PROJECT: | xxx |  | PROJECT NO.: | xxx
CREATED BY: | xxx |  | CREATED DATE: | xxx
CHECKED BY: | xxx |  | REVISED DATE: | xxx
THIS TAB IS A LOOKUP TABLE.
DO NOT EDIT THE CONTENT OF THIS TAB.
"C" Values for Conductors (BASED ON IEEE STD 241-1990, IEEE Std 242-1986)
| CU |  |  |  | AL |  |  |  |  | Busway
Cable | Single |  | 3C |  | Single |  | 3C |  |  | Ampacity | Plug-In | Feeder |  | High Impedance
Conduit | Steel | PVC | Steel | PVC | Steel | PVC | Steel | PVC |  |  | Copper | Aluminum | Copper | Aluminum | Copper
14 | 389 | 389 | 389 | 389 | 237 | 237 | 237 | 237 |  | 225 | 28700 | 23000 | 18700 | 12000 | -
12 | 617 | 617 | 617 | 617 | 376 | 376 | 376 | 376 |  | 400 | 38900 | 34700 | 23900 | 21300 | -
10 | 981 | 982 | 982 | 982 | 599 | 599 | 599 | 599 |  | 600 | 41000 | 38300 | 36500 | 31300 | -
8 | 1557 | 1559 | 1559 | 1560 | 951 | 952 | 952 | 952 |  | 800 | 46100 | 57500 | 49300 | 44100 | -
6 | 2425 | 2430 | 2431 | 2433 | 1481 | 1482 | 1482 | 1482 |  | 1000 | 69400 | 89300 | 62900 | 56200 | 15600
4 | 3806 | 3826 | 3830 | 3838 | 2346 | 2350 | 2351 | 2353 |  | 1200 | 94300 | 97100 | 76900 | 69900 | 16100
3 | 4774 | 4811 | 4820 | 4833 | 2952 | 2961 | 2963 | 2966 |  | 1350 | 119000 | 104200 | 90100 | 84000 | 17500
2 | 5907 | 6044 | 5989 | 6087 | 3713 | 3730 | 3734 | 3740 |  | 1600 | 129900 | 120500 | 101000 | 90900 | 19200
1 | 7293 | 7493 | 7454 | 7579 | 4645 | 4678 | 4686 | 4699 |  | 2000 | 142900 | 135100 | 134200 | 125000 | 20400
1/0 | 8925 | 9317 | 9210 | 9473 | 5777 | 5838 | 5852 | 5876 |  | 2500 | 143800 | 156300 | 180500 | 166700 | 21700
2/0 | 10755 | 11424 | 11245 | 11703 | 7187 | 7301 | 7327 | 7373 |  | 3000 | 144900 | 175400 | 204100 | 188700 | 23800
3/0 | 12844 | 13923 | 13656 | 14410 | 8826 | 9110 | 9077 | 9243 |  | 4000 | - | - | 277800 | 256400 | -
4/0 | 15082 | 16673 | 16392 | 17483 | 10741 | 11174 | 11185 | 11409
250 | 16483 | 18594 | 18311 | 19779 | 12122 | 12862 | 12797 | 13236
300 | 18177 | 20868 | 20617 | 22525 | 13910 | 14923 | 14917 | 15495 | Notes / Assumptions:
350 | 19704 | 22737 | 22646 | 24904 | 15484 | 16813 | 16795 | 17635 | Plug-In CU
400 | 20566 | 24297 | 24253 | 26916 | 16671 | 18506 | 18462 | 19588 | Copper_Normal
500 | 22185 | 26706 | 26980 | 30096 | 18756 | 21391 | 21395 | 23018 | Aluminum_Normal
600 | 22965 | 28033 | 28752 | 32154 | 20093 | 23451 | 23633 | 25708 | Copper_HighZ
750 | 24137 | 29735 | 31051 | 34605 | 21766 | 25976 | 26432 | 29036 | Aluminum_HighZ
1000 | 25278 | 31491 | 33864 | 37197 | 23478 | 28779 | 29865 | 32938