## 3W - 3Ph 3W+G
FEEDER SCHEDULE
COPPER/ALUMINUM: 3 PHASE, 3 WIRE + GROUND
NOMINAL AMPACITY | TAG | NUMBER OF SETS | CONDUIT SIZE (MIN) | PHASE CONDUCTORS (AWG or kcmil) | GROUND CONDUCTOR (AWG or kcmil)
20 | 203 | 1 | 3/4" | (3) 12 CU | 12 CU
30 | 303 | 1 | 3/4" | (3) 10 CU | 10 CU
40 | 403 | 1 | 3/4" | (3) 8 CU | 10 CU
50 | 503 | 1 | 3/4" | (3) 6 CU | 10 CU
60 | 603 | 1 | 1" | (3) 4 CU | 10 CU
70 | 703 | 1 | 1" | (3) 4 CU | 8 CU
80 | 803 | 1 | 1 1/4" | (3) 3 CU | 8 CU
90 | 903 | 1 | 1 1/4" | (3) 2 CU | 8 CU
100 | 1003 | 1 | 1 1/2" | (3) 1/0 AL | 8 CU
110 | 1103 | 1 | 1 1/2" | (3) 1/0 AL | 6 CU
125 | 1253 | 1 | 1 1/2" | (3) 2/0 AL | 6 CU
150 | 1503 | 1 | 2" | (3) 3/0 AL | 6 CU
175 | 1753 | 1 | 2" | (3) 4/0 AL | 6 CU
200 | 2003 | 1 | 2 1/2" | (3) 250 AL | 6 CU
225 | 2253 | 1 | 2 1/2" | (3) 350 AL | 4 CU
250 | 2503 | 1 | 2 1/2" | (3) 350 AL | 4 CU
300 | 3003 | 2 | 2" | (3) 3/0 AL | 4 CU
350 | 3503 | 2 | 2" | (3) 4/0 AL | 3 CU
400 | 4003 | 2 | 2 1/2" | (3) 250 AL | 3 CU
450 | 4503 | 2 | 2 1/2" | (3) 350 AL | 3 CU
500 | 5003 | 2 | 2 1/2" | (3) 350 AL | 3 CU
600 | 6003 | 2 | 3" | (3) 500 AL | 1 CU
800 | 8003 | 3 | 3" | (3) 500 AL | 1/0 CU
1000 | 10003 | 4 | 3" | (3) 350 AL | 4/0 AL
1200 | 12003 | 4 | 3" | (3) 500 AL | 250 AL
1600 | 16003 | 6 | 3" | (3) 500 AL | 350 AL
2000 | 20003 | 6 | 4" | (3) 750 AL | 500 AL
2500 | 25003 | 7 | 4" | (3) 750 AL | 500 AL
3000 | 30003 | 8 | 4" | (3) 750 AL | 750 AL
4000 | 40003 | 11 | 4" | (3) 750 AL | 750 AL
NOTES:
1. REFER TO SPECIFICATIONS FOR INSULATION TYPE PER WIRE SIZE.
2. MINIMUM CONDUIT SIZES IDENTIFIED MEET MAXIMUM 40% FILL FOR EMT, RMC AND PVC SCHEDULE 40.
3. FOR FEEDER RATINGS 100AMPS OR LESS, ACTUAL AMPACITY IS CALCULATED BY THOSE GIVEN IN NEC 310.15(B)(16), 60DEG C.
4. FOR FEEDER RATINGS GREATER THAN 100AMPS, ACTUAL AMPACITY IS CALCULATED BY THOSE GIVEN IN NEC 310.15(B)(16), 75DEG C.
5. THIS IS A STANDARD FEEDER SCHEDULE. SOME FEEDER TYPES MAY APPEAR IN THIS SCHEDULE THAT ARE NOT USED ON THIS PROJECT.

## 4W - 3Ph 4W+G
FEEDER SCHEDULE
COPPER/ALUMINUM: 3 PHASE, 4 WIRE + GROUND
NOMINAL AMPACITY | TAG | NUMBER OF SETS | CONDUIT SIZE (MIN) | PHASE & NEUTRAL CONDUCTORS (AWG or kcmil) | GROUND CONDUCTOR (AWG or kcmil)
20 | 204 | 1 | 3/4" | (4) 12 CU | 12 CU
30 | 304 | 1 | 3/4" | (4) 10 CU | 10 CU
40 | 404 | 1 | 3/4" | (4) 8 CU | 10 CU
50 | 504 | 1 | 1" | (4) 6 CU | 10 CU
60 | 604 | 1 | 1 1/4" | (4) 4 CU | 10 CU
70 | 704 | 1 | 1 1/4" | (4) 4 CU | 8 CU
80 | 804 | 1 | 1 1/4" | (4) 3 CU | 8 CU
90 | 904 | 1 | 1 1/4" | (4) 2 CU | 8 CU
100 | 1004 | 1 | 2" | (4) 1/0 AL | 6 CU
110 | 1104 | 1 | 2" | (4) 2/0 AL | 6 CU
125 | 1254 | 1 | 2" | (4) 3/0 AL | 6 CU
150 | 1504 | 1 | 2 1/2" | (4) 4/0 AL | 6 CU
175 | 1754 | 1 | 2 1/2" | (4) 250 AL | 4 CU
200 | 2004 | 1 | 3" | (4) 350 AL | 6 CU
225 | 2254 | 1 | 3 1/2" | (4) 350 AL | 6 CU
250 | 2504 | 1 | 3 1/2" | (4) 500 AL | 4 CU
300 | 3004 | 2 | 2 1/2" | (4) 4/0 AL | 4 CU
350 | 3504 | 2 | 2 1/2" | (4) 250 AL | 3 CU
400 | 4004 | 2 | 3" | (4) 350 AL | 3 CU
450 | 4504 | 2 | 3 1/2" | (4) 500 AL | 3 CU
500 | 5004 | 2 | 3 1/2" | (4) 500 AL | 3 CU
600 | 6004 | 3 | 3" | (4) 350 AL | 1 CU
800 | 8004 | 3 | 3 1/2" | (4) 500 AL | 1/0 CU
1000 | 10004 | 4 | 3 1/2" | (4) 500 AL | 4/0 AL
1200 | 12004 | 5 | 3 1/2" | (4) 500 AL | 250 AL
1600 | 16004 | 6 | 3 1/2" | (4) 500 AL | 350 AL
2000 | 20004 | 8 | 4" | (4) 500 AL | 500 AL
2500 | 25004 | 9 | 4" | (4) 500 AL | 500 AL
3000 | 30004 | 11 | 4" | (4) 500 AL | 500 AL
4000 | 40004 | 15 | 4" | (4) 500 AL | 500 AL
NOTES:
1. REFER TO SPECIFICATIONS FOR INSULATION TYPE PER WIRE SIZE.
2. MINIMUM CONDUIT SIZES IDENTIFIED MEET MAXIMUM 40% FILL FOR EMT, RMC AND PVC SCHEDULE 40.
3. NEUTRAL CONDUCTORS ARE CONSIDERED CURRENT CARRYING, THEREFORE AMPACITY ADJUSTMENTS HAVE BEEN INCLUDED IN ACCORDANCE WITH NEC TABLE 310.15(B)(3)(a) TO ACCOMMODATE FOUR (4) CURRENT CARRYING CONDUCTORS IN A SINGLE RACEWAY.
4. ADJUSTED CONDUCTOR AMPACITIES ARE CALCULATED BASED ON THOSE GIVEN FOR 90DEG C CONDUCTORS IN ACCORDANCE WITH NEC 310.15(B) AND TABLE NEC 310.15(B)(16). FOR FEEDER RATINGS 100AMPS OR LESS, KEEP THE ADJUSTED AMPACITY AT OR BELOW THE 60DEG C RATING. FOR FEEDER RATINGS OVER 100AMPS, KEEP THE ACTUAL AMPACITY AT OR BELOW THE 75DEG C RATING.
5. THIS IS A STANDARD FEEDER SCHEDULE. SOME FEEDER TYPES MAY APPEAR IN THIS SCHEDULE THAT ARE NOT USED ON THIS PROJECT.