## 2001-5000V
MEDIUM-VOLTAGE FEEDER SCHEDULE (2001-5000V)
COPPER: 3 PHASE, 3 WIRE + GROUND
FOR SINGLE CIRCUIT, THREE SINGLE-INSULATED COPPER CONDUCTORS IN ISOLATED UNDERGROUND ELECTRICAL DUCT
BASED ON NEC TABLE 315.60(C)(11), SINGLE CIRCUIT, CONDUCTOR TEMPERATURE OF 90°C (194°F), IN PVC CONDUIT
TAG | NOMINAL AMPACITY | NUMBER OF SETS | CONDUIT SIZE (MIN) | PHASE CONDUCTORS (AWG or kcmil) | GROUND CONDUCTOR (AWG or kcmil)
5K703 | 70 | 1 | 2 1/2" | 3#6 | 1#6
5K1003 | 100 | 1 | 2 1/2" | 3#4 | 1#6
5K1253 | 125 | 1 | 2 1/2" | 3#2 | 1#6
5K1503 | 150 | 1 | 3" | 3#1 | 1#6
5K2003 | 200 | 1 | 3" | 3#2/0 | 1#6
5K2503 | 250 | 1 | 3" | 3#3/0 | 1#4
5K3003 | 300 | 1 | 3 1/2" | 3#250 | 1#4
5K4003 | 400 | 1 | 4" | 3#500 | 1#2
5K6003 | 600 | 1 | 5" | 3#1000 | 1#1
NOTES:
1. REFER TO SPECIFICATIONS FOR INSULATION TYPE PER WIRE SIZE.
2. MINIMUM CONDUIT SIZES IDENTIFIED MEET MAXIMUM 40% FILL FOR EMT, RMC AND PVC SCHEDULE 40.
3. THIS IS A STANDARD FEEDER SCHEDULE. SOME FEEDER TYPES MAY APPEAR IN THIS SCHEDULE THAT ARE NOT USED ON THIS PROJECT.
4. CONDUIT SIZES NOTED ON SINGLE-LINE DIAGRAM OR ON PLANS SUPERSEDE SIZES NOTED ABOVE IF LARGER. REFER TO SPECIFICATIONS FOR INFORMATION ON CONDUIT TYPE, FITTINGS AND ELBOWS, AND DUCT BANK CONSTRUCTION.
5. PROVIDE THERMAL CALCULATIONS AND VOLTAGE DROP CALCULATIONS FOR UNDERGROUND FEEDERS. PROVIDE TO OWNER FOR APPROVAL PRIOR TO PROCUREMENT AND INSTALLATION.

## 5001-15000V
MEDIUM-VOLTAGE FEEDER SCHEDULE (5001-15000V)
COPPER: 3 PHASE, 3 WIRE + GROUND
FOR SINGLE CIRCUIT, THREE SINGLE-INSULATED COPPER CONDUCTORS IN ISOLATED UNDERGROUND ELECTRICAL DUCT
BASED ON NEC TABLE 315.60(C)(11), SINGLE CIRCUIT, CONDUCTOR TEMPERATURE OF 90°C (194°F), IN PVC CONDUIT
TAG | NOMINAL AMPACITY | NUMBER OF SETS | CONDUIT SIZE (MIN) | PHASE CONDUCTORS (AWG or kcmil) | GROUND CONDUCTOR (AWG or kcmil)
15K1503 | 150 | 1 | 3 1/2" | 3#2 | 1#2
15K2003 | 200 | 1 | 4" | 3#1/0 | 1#2
15K2503 | 250 | 1 | 4" | 3#3/0 | 1#2
15K3003 | 300 | 1 | 5" | 3#250 | 1#2
15K4003 | 400 | 1 | 5" | 3#500 | 1#2
15K6003 | 600 | 1 | 6" | 3#1000 | 1#1
NOTES:
1. REFER TO SPECIFICATIONS FOR INSULATION TYPE PER WIRE SIZE.
2. MINIMUM CONDUIT SIZES IDENTIFIED MEET MAXIMUM 40% FILL FOR EMT, RMC AND PVC SCHEDULE 40.
3. THIS IS A STANDARD FEEDER SCHEDULE. SOME FEEDER TYPES MAY APPEAR IN THIS SCHEDULE THAT ARE NOT USED ON THIS PROJECT.
4. CONDUIT SIZES NOTED ON SINGLE-LINE DIAGRAM OR ON PLANS SUPERSEDE SIZES NOTED ABOVE IF LARGER. REFER TO SPECIFICATIONS FOR INFORMATION ON CONDUIT TYPE, FITTINGS AND ELBOWS, AND DUCT BANK CONSTRUCTION.
5. PROVIDE THERMAL CALCULATIONS AND VOLTAGE DROP CALCULATIONS FOR UNDERGROUND FEEDERS. PROVIDE TO OWNER FOR APPROVAL PRIOR TO PROCUREMENT AND INSTALLATION.