## AWG 14–1
NEC TABLE 9 — AC Resistance & Reactance, 600V Cables, 3-Phase, 60 Hz, 75°C (167°F) — Three Single Conductors in Conduit
AWG 14 → 1 ¦ Source: NEC 2023 Chapter 9, Table 9 ¦ Blue = Ω/km (top row) ¦ Bold Dark Blue = Ω/1000 ft (bottom row)
Size (AWG or kcmil) | Xₗ (Reactance) for All Wires |  | Alternating-Current Resistance for Uncoated Copper Wires |  |  | Alternating-Current Resistance for Aluminum Wires |  |  | Effective Z at 0.85 PF for Uncoated Copper Wires |  |  | Effective Z at 0.85 PF for Aluminum Wires
| PVC, Aluminum Conduits | Steel Conduit | PVC Conduit | Aluminum Conduit | Steel Conduit | PVC Conduit | Aluminum Conduit | Steel Conduit | PVC Conduit | Aluminum Conduit | Steel Conduit | PVC Conduit | Aluminum Conduit | Steel Conduit
Ohms to Neutral per Kilometer (top) / Ohms to Neutral per 1000 Feet (bottom)
14 | 0.19 | 0.24 | 10.2 | 10.2 | 10.2 | — | — | — | 8.9 | 8.9 | 8.9 | — | — | —
| 0.058 | 0.073 | 3.1 | 3.1 | 3.1 | — | — | — | 2.7 | 2.7 | 2.7 | — | — | —
12 | 0.177 | 0.223 | 6.6 | 6.6 | 6.6 | 10.5 | 10.5 | 10.5 | 5.6 | 5.6 | 5.6 | 9.2 | 9.2 | 9.2
| 0.054 | 0.068 | 2 | 2 | 2 | 3.2 | 3.2 | 3.2 | 1.7 | 1.7 | 1.7 | 2.8 | 2.8 | 2.8
10 | 0.164 | 0.207 | 3.9 | 3.9 | 3.9 | 6.6 | 6.6 | 6.6 | 3.6 | 3.6 | 3.6 | 5.9 | 5.9 | 5.9
| 0.05 | 0.063 | 1.2 | 1.2 | 1.2 | 2 | 2 | 2 | 1.1 | 1.1 | 1.1 | 1.8 | 1.8 | 1.8
8 | 0.171 | 0.213 | 2.56 | 2.56 | 2.56 | 4.3 | 4.3 | 4.3 | 2.26 | 2.26 | 2.3 | 3.6 | 3.6 | 3.6
| 0.052 | 0.065 | 0.78 | 0.78 | 0.78 | 1.3 | 1.3 | 1.3 | 0.69 | 0.69 | 0.7 | 1.1 | 1.1 | 1.1
6 | 0.167 | 0.21 | 1.61 | 1.61 | 1.61 | 2.66 | 2.66 | 2.66 | 1.44 | 1.48 | 1.48 | 2.33 | 2.36 | 2.36
| 0.051 | 0.064 | 0.49 | 0.49 | 0.49 | 0.81 | 0.81 | 0.81 | 0.44 | 0.45 | 0.45 | 0.71 | 0.72 | 0.72
4 | 0.157 | 0.197 | 1.02 | 1.02 | 1.02 | 1.67 | 1.67 | 1.67 | 0.95 | 0.95 | 0.98 | 1.51 | 1.51 | 1.51
| 0.048 | 0.06 | 0.31 | 0.31 | 0.31 | 0.51 | 0.51 | 0.51 | 0.29 | 0.29 | 0.3 | 0.46 | 0.46 | 0.46
3 | 0.154 | 0.194 | 0.82 | 0.82 | 0.82 | 1.31 | 1.35 | 1.31 | 0.75 | 0.79 | 0.79 | 1.21 | 1.21 | 1.21
| 0.047 | 0.059 | 0.25 | 0.25 | 0.25 | 0.4 | 0.41 | 0.4 | 0.23 | 0.24 | 0.24 | 0.37 | 0.37 | 0.37
2 | 0.148 | 0.187 | 0.62 | 0.66 | 0.66 | 1.05 | 1.05 | 1.05 | 0.62 | 0.62 | 0.66 | 0.98 | 0.98 | 0.98
| 0.045 | 0.057 | 0.19 | 0.2 | 0.2 | 0.32 | 0.32 | 0.32 | 0.19 | 0.19 | 0.2 | 0.3 | 0.3 | 0.3
1 | 0.151 | 0.187 | 0.49 | 0.52 | 0.52 | 0.82 | 0.85 | 0.82 | 0.52 | 0.52 | 0.52 | 0.79 | 0.79 | 0.82
| 0.046 | 0.057 | 0.15 | 0.16 | 0.16 | 0.25 | 0.26 | 0.25 | 0.16 | 0.16 | 0.16 | 0.24 | 0.24 | 0.25

## 1-0 thru 1000 kcmil
NEC TABLE 9 — AC Resistance & Reactance, 600V Cables, 3-Phase, 60 Hz, 75°C (167°F) — Three Single Conductors in Conduit
1/0 → 1000 kcmil ¦ Source: NEC 2023 Chapter 9, Table 9 ¦ Blue = Ω/km (top row) ¦ Bold Dark Blue = Ω/1000 ft (bottom row)
Size (AWG or kcmil) | Xₗ (Reactance) for All Wires |  | Alternating-Current Resistance for Uncoated Copper Wires |  |  | Alternating-Current Resistance for Aluminum Wires |  |  | Effective Z at 0.85 PF for Uncoated Copper Wires |  |  | Effective Z at 0.85 PF for Aluminum Wires
| PVC, Aluminum Conduits | Steel Conduit | PVC Conduit | Aluminum Conduit | Steel Conduit | PVC Conduit | Aluminum Conduit | Steel Conduit | PVC Conduit | Aluminum Conduit | Steel Conduit | PVC Conduit | Aluminum Conduit | Steel Conduit
Ohms to Neutral per Kilometer (top) / Ohms to Neutral per 1000 Feet (bottom)
1/0 | 0.144 | 0.18 | 0.39 | 0.43 | 0.39 | 0.66 | 0.69 | 0.66 | 0.43 | 0.43 | 0.43 | 0.62 | 0.66 | 0.66
| 0.044 | 0.055 | 0.12 | 0.13 | 0.12 | 0.2 | 0.21 | 0.2 | 0.13 | 0.13 | 0.13 | 0.19 | 0.2 | 0.2
2/0 | 0.141 | 0.177 | 0.33 | 0.33 | 0.33 | 0.52 | 0.52 | 0.52 | 0.36 | 0.36 | 0.36 | 0.52 | 0.52 | 0.52
| 0.043 | 0.054 | 0.1 | 0.1 | 0.1 | 0.16 | 0.16 | 0.16 | 0.11 | 0.11 | 0.11 | 0.16 | 0.16 | 0.16
3/0 | 0.138 | 0.171 | 0.253 | 0.269 | 0.259 | 0.43 | 0.43 | 0.43 | 0.289 | 0.302 | 0.308 | 0.43 | 0.43 | 0.46
| 0.042 | 0.052 | 0.077 | 0.082 | 0.079 | 0.13 | 0.13 | 0.13 | 0.088 | 0.092 | 0.094 | 0.13 | 0.13 | 0.14
4/0 | 0.135 | 0.167 | 0.203 | 0.22 | 0.207 | 0.33 | 0.36 | 0.33 | 0.243 | 0.256 | 0.262 | 0.36 | 0.36 | 0.36
| 0.041 | 0.051 | 0.062 | 0.067 | 0.063 | 0.1 | 0.11 | 0.1 | 0.074 | 0.078 | 0.08 | 0.11 | 0.11 | 0.11
250 | 0.135 | 0.171 | 0.171 | 0.187 | 0.177 | 0.279 | 0.295 | 0.282 | 0.217 | 0.23 | 0.24 | 0.308 | 0.322 | 0.33
| 0.041 | 0.052 | 0.052 | 0.057 | 0.054 | 0.085 | 0.09 | 0.086 | 0.066 | 0.07 | 0.073 | 0.094 | 0.098 | 0.1
300 | 0.135 | 0.167 | 0.144 | 0.161 | 0.148 | 0.233 | 0.249 | 0.236 | 0.194 | 0.207 | 0.213 | 0.269 | 0.282 | 0.289
| 0.041 | 0.051 | 0.044 | 0.049 | 0.045 | 0.071 | 0.076 | 0.072 | 0.059 | 0.063 | 0.064 | 0.082 | 0.086 | 0.088
350 | 0.131 | 0.164 | 0.125 | 0.141 | 0.128 | 0.2 | 0.217 | 0.207 | 0.174 | 0.19 | 0.197 | 0.24 | 0.253 | 0.262
| 0.04 | 0.05 | 0.038 | 0.043 | 0.039 | 0.061 | 0.066 | 0.063 | 0.053 | 0.058 | 0.06 | 0.073 | 0.077 | 0.08
400 | 0.131 | 0.161 | 0.108 | 0.125 | 0.115 | 0.177 | 0.194 | 0.18 | 0.161 | 0.174 | 0.184 | 0.217 | 0.233 | 0.24
| 0.04 | 0.049 | 0.033 | 0.038 | 0.035 | 0.054 | 0.059 | 0.055 | 0.049 | 0.053 | 0.056 | 0.066 | 0.071 | 0.073
500 | 0.128 | 0.157 | 0.089 | 0.105 | 0.095 | 0.141 | 0.157 | 0.148 | 0.141 | 0.157 | 0.164 | 0.187 | 0.2 | 0.21
| 0.039 | 0.048 | 0.027 | 0.032 | 0.029 | 0.043 | 0.048 | 0.045 | 0.043 | 0.048 | 0.05 | 0.057 | 0.061 | 0.064
600 | 0.128 | 0.157 | 0.075 | 0.092 | 0.082 | 0.118 | 0.135 | 0.125 | 0.131 | 0.144 | 0.154 | 0.167 | 0.18 | 0.19
| 0.039 | 0.048 | 0.023 | 0.028 | 0.025 | 0.036 | 0.041 | 0.038 | 0.04 | 0.044 | 0.047 | 0.051 | 0.055 | 0.058
750 | 0.125 | 0.157 | 0.062 | 0.079 | 0.069 | 0.095 | 0.112 | 0.102 | 0.118 | 0.131 | 0.141 | 0.148 | 0.161 | 0.171
| 0.038 | 0.048 | 0.019 | 0.024 | 0.021 | 0.029 | 0.034 | 0.031 | 0.036 | 0.04 | 0.043 | 0.045 | 0.049 | 0.052
1000 | 0.121 | 0.151 | 0.049 | 0.062 | 0.059 | 0.075 | 0.089 | 0.082 | 0.105 | 0.118 | 0.131 | 0.128 | 0.138 | 0.151
| 0.037 | 0.046 | 0.015 | 0.019 | 0.018 | 0.023 | 0.027 | 0.025 | 0.032 | 0.036 | 0.04 | 0.039 | 0.042 | 0.046